## DoE typ.pump duty (hidden)
Working Hours | p.u. Power Consumed - PWM Inverter | p.u. Required Flow Rate throughout the working day | p.u. Power Consumed - Constant Volume By-Pass Valve
1 | 1.1 | 1 | 1.1
2 | 0.829 | 0.9 | 1.1
3 | 0.423 | 0.7 | 1.1
4 | 0.236 | 0.55 | 1.1
5 | 0.134 | 0.4 | 1.1
6 | 0.097 | 0.3 | 1.1
7 | 0.097 | 0.3 | 1.1
8 | 0.103 | 0.32 | 1.1
9 | 0.125 | 0.38 | 1.1
10 | 0.161 | 0.45 | 1.1

## Chart6 (hidden)
calculated from the poly

## Power Saving sheet(with PUMP) (hidden)
PUMP AND FAN LOAD v POWER CONSUMED
[7 empty] | pu |  |  | Savings against PWM
POWER
pu
|  | FLOW RATE | PWM | EEC | Saving over EEC |  | Disc Throttle | Saving over Disc Throttle |  | Inlet Guide Vane | Saving over Inlet Guide Vane | Damper(Fwd) | Saving over Damper(Forward Curved centrifugal Fan) | Damper(Back) | Saving over Damper(Backward Curved centrifugal Fan) |  | PWM power | Pump - Constant Volume | Saving over Pump - Constant Volume
|  | 0.2 | 0.05 |  |  |  | 0.35 | 0.3 |  | 0.39 | 0.34 | 0.505 | 0.455 | 0.555 | 0.505 |  |  | 1.1 | 1.1
|  | 0.3 | 0.07 | 0.2 | 0.13 |  | 0.35 | 0.28 |  | 0.415 | 0.345 | 0.505 | 0.435 | 0.64 | 0.57 |  | 0.097 | 1.1 | 1.003
|  | 0.32 | 0.075 | 0.205 | 0.13 |  | 0.355 | 0.28 |  | 0.42 | 0.345 | 0.51 | 0.435 | 0.655 | 0.58 |  | 0.103 | 1.1 | 0.997
|  | 0.38 | 0.1 | 0.245 | 0.145 |  | 0.36 | 0.26 |  | 0.445 | 0.345 | 0.53 | 0.43 | 0.705 | 0.605 |  | 0.125 | 1.1 | 0.975
|  | 0.4 | 0.1093 | 0.26 | 0.1507 |  | 0.365 | 0.2557 |  | 0.45 | 0.3407 | 0.54 | 0.4307 | 0.72 | 0.6107 |  | 0.134 | 1.1 | 0.966
|  | 0.5 | 0.19 | 0.365 | 0.175 |  | 0.39 | 0.2 |  | 0.5 | 0.31 | 0.6 | 0.41 | 0.8 | 0.61 |  |  | 1.1
|  | 0.6 | 0.295 | 0.5 | 0.205 |  | 0.445 | 0.15 |  | 0.57 | 0.275 | 0.69 | 0.395 | 0.875 | 0.58 |  |  | 1.1
|  | 0.7 | 0.425 | 0.65 | 0.225 |  | 0.52 | 0.095 |  | 0.65 | 0.225 | 0.8 | 0.375 | 0.95 | 0.525 |  | 0.423 | 1.1 | 0.677
|  | 0.8 | 0.6 | 0.82 | 0.22 |  | 0.64 | 0.04 |  | 0.77 | 0.17 | 0.95 | 0.35 | 1.02 | 0.42 |  |  | 1.1 | 1.1
|  | 0.9 | 0.81 | 1.02 | 0.21 |  | 0.81 | 0 |  | 0.92 | 0.11 | 1.125 | 0.315 | 1.08 | 0.27 |  | 0.829 | 1.1 | 0.271
|  | 1 | 1.1 | 1.24 | 0.14 |  | 1.18 | 0.08 |  | 1.18 | 0.08 | 1.35 | 0.25 | 1.14 | 0.04 |  | 1.1 | 1.1 | 0
contant for powers of x below
|  |  | 6th | 5th | 4th | 3rd | 2ed | 1st | CONSTANT |  | Equation |  |  |  |  | FLOW RATE | PWM power
Output Damper |  |  | 11.904 | -45.938 | 68.673 | -51.21 | 18.472 | -2.4253 | 0.5648 | [6 empty] | 0.3 | 0.097
Output Damper |  |  | 11.715 | -46.519 | 72.614 | -57.078 | 23.635 | -4.9755 | 0.8591 | [6 empty] | 0.32 | 0.103
Output Damper |  |  | 0 | 2.4349 | -5.9778 | 5.9408 | -3.6661 | 1.1257 | 0.222 | [6 empty] | 0.38 | 0.125
Output Damper |  |  | 49.143 | -163.84 | 218.75 | -147.93 | 52.34 | -9.3296 | 0.9549 | [6 empty] | 0.4 | 0.134
Output Damper |  |  | 0 | -6.8804 | 21.142 | -26.304 | 16.1 | -4.5049 | 0.5877 | [6 empty] | 0.7 | 0.423
[16 empty] | 0.9 | 0.829
[16 empty] | 1 | 1.1
| Column for x values |  | p.u. Savings using PMW Inverter as replacent for:-
| Volume Flow p.u. |  | Constant Volume - no control | Output Damper | Input Damper | Inlet Guide Vane | Disc throttle | EddyCurrentCoupling
| 0.2 |  | 0.92882 | 0.50488 | 0.45482 | 0.33924 | 0.29986 | 0.15191
| 0.25 |  | 0.91623 | 0.53912 | 0.44165 | 0.34615 | 0.28883 | 0.13259
| 0.3 |  | 0.90301 | 0.57032 | 0.43617 | 0.34766 | 0.28208 | 0.12955
| 0.35 |  | 0.88687 | 0.59427 | 0.43262 | 0.34469 | 0.27113 | 0.13658
| 0.4 |  | 0.86602 | 0.60914 | 0.42806 | 0.33782 | 0.25351 | 0.14906
| 0.45 |  | 0.83908 | 0.61467 | 0.42148 | 0.32734 | 0.23019 | 0.16378
| 0.5 |  | 0.80489 | 0.6114 | 0.41305 | 0.3134 | 0.20358 | 0.17861
| 0.55 |  | 0.77 | 0.60013 | 0.4035 | 0.29608 | 0.17611 | 0.19227
| 0.6 |  | 0.722 | 0.58145 | 0.39358 | 0.27545 | 0.14928 | 0.20408
| 0.65 |  | 0.67 | 0.55543 | 0.3838 | 0.25171 | 0.12338 | 0.21368
| 0.7 |  | 0.61 | 0.52142 | 0.37408 | 0.22526 | 0.097701 | 0.2208
| 0.75 |  | 0.54 | 0.47803 | 0.36375 | 0.19677 | 0.071247 | 0.22498
| 0.8 |  | 0.465 | 0.42318 | 0.35153 | 0.16731 | 0.044111 | 0.22533
| 0.85 |  | 0.378 | 0.35436 | 0.33573 | 0.13841 | 0.019326 | 0.22023
| 0.9 |  | 0.27 | 0.26896 | 0.31451 | 0.11218 | 0.0052885 | 0.20713
| 0.95 |  | 0.15 | 0.16474 | 0.28636 | 0.091377 | 0.01874 | 0.18227
| 1 |  | 0.02 | 0.0405 | 0.2506 | 0.0795 | 0.0883 | 0.1404
| Column for x values |  | Pump Power Consumption | p.u. Savings using PMW Inverter as replacent for:-
| Volume Flow p.u. |  |  | Constant Volume - no control
| 0.2 |  | 0.071178 | 0.92882
| 0.25 |  | 0.083767 | 0.91623
| 0.3 |  | 0.096988 | 0.90301
| 0.35 |  | 0.11313 | 0.88687
| 0.4 |  | 0.13398 | 0.86602
| 0.45 |  | 0.16092 | 0.83908
| 0.5 |  | 0.19511 | 0.80489
| 0.55 |  | 0.23755 | 0.76245
| 0.6 |  | 0.28913 | 0.71087
| 0.65 |  | 0.35066 | 0.64934
| 0.7 |  | 0.42291 | 0.57709
| 0.75 |  | 0.50651 | 0.49349
| 0.8 |  | 0.60195 | 0.39805
| 0.85 |  | 0.70945 | 0.29055
| 0.9 |  | 0.82884 | 0.17116
| 0.95 |  | 0.95943 | 0.04057
| 1 |  | 1.0998 | -0.0998
Note on B35: Flow Value for which power saving is to be calculated
Note on B57: Flow Value for which power saving is to be calculated

## Styised by poly for publication (hidden)
verses other methods of flow control

## CALCULATION SHEET
Company: |  | IMO Precision Controls |  |  |  |  | Application name: |  | Jaguar VXM
Fill in the 'green' boxes for the current or estimated flow rates to get a potential annual cost saving when using IMO Jaguar VSD. Savings are shown against six existing Flow Control options
| Days per week = |  |  | 5 |  | SELECT EXISTING FLOW CONTROL SYSTEM TO BE REPLACED - enter '1' in the Box to indicate current control method
| Weeks pa = |  |  | 52
| Flow | [6 empty] | ENERGY SAVINGS |  | £ SAVINGS |  | PAYBACK PERIOD
| Rate |  | Hours |  |  |  |  | per YEAR |  | per YEAR
| % |  | per day
| 20 |  |  |  | 0 | Output Damper (or Valve) | 1 | 45894.2851 | kWatt-hr | 2294.7143 |  | 1.0677 | Years
| 25 |  |  |  | 0
| 30 | 0 |  | 0 | 0 | Inlet Damper |  | 38123.7896 | kWatt-hr | 0 |  | #DIV/0! | Years
| 35 |  |  |  | 0
| 40 | 0 |  | 0 | 0 | Inlet Guide Vane |  | 18144.618 | kWatt-hr | 0 |  | #DIV/0! | Years
| 45 | 0 |  | 0 | 0
| 50 |  |  |  | 0 | Disc Throttle |  | 4783.9334 | kWatt-hr | 0 |  | #DIV/0! | Years
| 55 | 0 |  | 0 | 0
| 60 |  |  |  | 0 | Eddy Current Coupling |  | 24436.8456 | kWatt-hr | 0 |  | #DIV/0! | Years
| 65 |  |  |  | 0
| 70 | 0 |  | 0 | 0 | Constant flow - no control |  | 43168.7971 | kWatt-hr | 0 |  | #DIV/0! | Years
| 75 |  |  |  | 0
| 80 |  | 16 |  | 832
| 85 |  |  |  | 0 |  |  | Cost of Inverter (£) |  | 1950
| 90 |  |  |  | 0 | Motor size (kW) = | 30
| 95 |  |  |  | 0 |  |  | Cost of Installation (£) |  | 500
| 100 |  |  |  | 0 | Avge. Elec. Cost = | 5
[6 empty] | (pence/kW-hr) |  | TOTAL RETROFIT COST |  | 2450 | 2450

## Sheet1 (hidden)
PUMP AND FAN LOAD v POWER CONSUMED
[7 empty] | pu |  |  | Savings against PWM
POWER
pu
|  | FLOW RATE | PWM | EEC | Saving over EEC |  | Disc Throttle | Saving over Disc Throttle |  | Inlet Guide Vane | Saving over Inlet Guide Vane | Damper(Fwd) | Saving over Damper(Forward Curved centrifugal Fan) | Damper(Back) | Saving over Damper(Backward Curved centrifugal Fan)
|  | 0.2 | 0.05 |  |  |  | 0.35 | 0.3 |  | 0.39 | 0.34 | 0.505 | 0.455 | 0.555 | 0.505
|  | 0.3 | 0.07 | 0.2 | 0.13 |  | 0.35 | 0.28 |  | 0.415 | 0.345 | 0.505 | 0.435 | 0.64 | 0.57
|  | 0.32 | 0.075 | 0.205 | 0.13 |  | 0.355 | 0.28 |  | 0.42 | 0.345 | 0.51 | 0.435 | 0.655 | 0.58
|  | 0.38 | 0.1 | 0.245 | 0.145 |  | 0.36 | 0.26 |  | 0.445 | 0.345 | 0.53 | 0.43 | 0.705 | 0.605
|  | 0.4 | 0.1093 | 0.26 | 0.1507 |  | 0.365 | 0.2557 |  | 0.45 | 0.3407 | 0.54 | 0.4307 | 0.72 | 0.6107
|  | 0.5 | 0.19 | 0.365 | 0.175 |  | 0.39 | 0.2 |  | 0.5 | 0.31 | 0.6 | 0.41 | 0.8 | 0.61
|  | 0.6 | 0.295 | 0.5 | 0.205 |  | 0.445 | 0.15 |  | 0.57 | 0.275 | 0.69 | 0.395 | 0.875 | 0.58
|  | 0.7 | 0.425 | 0.65 | 0.225 |  | 0.52 | 0.095 |  | 0.65 | 0.225 | 0.8 | 0.375 | 0.95 | 0.525
|  | 0.8 | 0.6 | 0.82 | 0.22 |  | 0.64 | 0.04 |  | 0.77 | 0.17 | 0.95 | 0.35 | 1.02 | 0.42
|  | 0.9 | 0.81 | 1.02 | 0.21 |  | 0.81 | 0 |  | 0.92 | 0.11 | 1.125 | 0.315 | 1.08 | 0.27
|  | 1 | 1.1 | 1.24 | 0.14 |  | 1.18 | 0.08 |  | 1.18 | 0.08 | 1.35 | 0.25 | 1.14 | 0.04
contant for powers of x below
|  |  | 6th | 5th | 4th | 3rd | 2ed | 1st | CONSTANT |  | Equation
Damper Backward curved centrifuge |  |  | 11.904 | -45.938 | 68.673 | -51.21 | 18.472 | -2.4253 | 0.5648
Damper Forward curved centrifuge |  |  | 11.715 | -46.519 | 72.614 | -57.078 | 23.635 | -4.9755 | 0.8591
Inlet guide vane |  |  | 0 | 2.4349 | -5.9778 | 5.9408 | -3.6661 | 1.1257 | 0.222
Disc throttle |  |  | 49.143 | -163.84 | 218.75 | -147.93 | 52.34 | -9.3296 | 0.9549
EEC |  |  | 0 | -6.8804 | 21.142 | -26.304 | 16.1 | -4.5049 | 0.5877
| Column for x values |  | p.u. Savings using PMW Invert as replacent
| Volume Flow p.u. |  | for:- | Damper(Back') | Damper(Fwd) | Inlet Guide Vane | Disc throttle | EEC
| 0.2 |  |  | 0.50488 | 0
| 0.25 |  |  | 0.53912
| 0.3 |  |  | 0.57032
| 0.35 |  |  | 0.59427
| 0.4 |  |  | 0.60914
| 0.45 |  |  | 0.61467
| 0.5 |  |  | 0.6114
| 0.55 |  |  | 0.60013
| 0.6 |  |  | 0.58145
| 0.65 |  |  | 0.55543
| 0.7 |  |  | 0.52142
| 0.75 |  |  | 0.47803
| 0.8 |  |  | 0.42318
| 0.85 |  |  | 0.35436
| 0.9 |  |  | 0.26896
| 0.95 |  |  | 0.16474
| 1 |  |  | 0.0405
Note on B35: Flow Value for which power saving is to be calculated

## Energy saving sheet (hidden)
PUMP AND FAN LOAD v POWER CONSUMED
[7 empty] | pu |  |  | Savings against PWM
POWER
pu
|  | FLOW RATE | PWM | ECC | Saving over ECC |  | Disc Throttle | Saving over Disc Throttle |  | Inlet Guide Vane | Saving over Inlet Guide Vane | Damper(Fwd) | Saving over Damper(Forward Curved centrifugal Fan) | Damper(Back) | Saving over Damper(Backward Curved centrifugal Fan)
|  | 0.2 | 0.05 |  |  |  | 0.35 | 0.3 |  | 0.39 | 0.34 | 0.505 | 0.455 | 0.555 | 0.505
|  | 0.3 | 0.07 | 0.2 | 0.13 |  | 0.35 | 0.28 |  | 0.415 | 0.345 | 0.505 | 0.435 | 0.64 | 0.57
|  | 0.32 | 0.075 | 0.205 | 0.13 |  | 0.355 | 0.28 |  | 0.42 | 0.345 | 0.51 | 0.435 | 0.655 | 0.58
|  | 0.38 | 0.1 | 0.245 | 0.145 |  | 0.36 | 0.26 |  | 0.445 | 0.345 | 0.53 | 0.43 | 0.705 | 0.605
|  | 0.4 | 0.1093 | 0.26 | 0.1507 |  | 0.365 | 0.2557 |  | 0.45 | 0.3407 | 0.54 | 0.4307 | 0.72 | 0.6107
|  | 0.5 | 0.19 | 0.365 | 0.175 |  | 0.39 | 0.2 |  | 0.5 | 0.31 | 0.6 | 0.41 | 0.8 | 0.61
|  | 0.6 | 0.295 | 0.5 | 0.205 |  | 0.445 | 0.15 |  | 0.57 | 0.275 | 0.69 | 0.395 | 0.875 | 0.58
|  | 0.7 | 0.425 | 0.65 | 0.225 |  | 0.52 | 0.095 |  | 0.65 | 0.225 | 0.8 | 0.375 | 0.95 | 0.525
|  | 0.8 | 0.6 | 0.82 | 0.22 |  | 0.64 | 0.04 |  | 0.77 | 0.17 | 0.95 | 0.35 | 1.02 | 0.42
|  | 0.9 | 0.81 | 1.02 | 0.21 |  | 0.81 | 0 |  | 0.92 | 0.11 | 1.125 | 0.315 | 1.08 | 0.27
|  | 1 | 1.1 | 1.24 | 0.14 |  | 1.18 | 0.08 |  | 1.18 | 0.08 | 1.35 | 0.25 | 1.14 | 0.04
Motor Kw (transfered from "calc sheet")
30
contant for powers of x below
|  |  | 6th | 5th | 4th | 3rd | 2ed | 1st | CONSTANT |  | Equation
Output Damper |  |  | 11.904 | -45.938 | 68.673 | -51.21 | 18.472 | -2.4253 | 0.5648
Inlet Damper |  |  | 11.715 | -46.519 | 72.614 | -57.078 | 23.635 | -4.9755 | 0.8591
Inlet guide vane |  |  | 0 | 2.4349 | -5.9778 | 5.9408 | -3.6661 | 1.1257 | 0.222
Disc throttle |  |  | 49.143 | -163.84 | 218.75 | -147.93 | 52.34 | -9.3296 | 0.9549
EddyCurrentCoupling |  |  | 0 | -6.8804 | 21.142 | -26.304 | 16.1 | -4.5049 | 0.5877
| Column for x values |  | p.u. Savings using PWM Inverter as replacent for:-
| Volume Flow p.u. |  |  | Damper(Back') | Damper(Fwd) | Inlet Guide Vane | Disc throttle | ECC
| 0.2 |  |  | 0.50488 | 0.45482 | 0.33924 | 0.29986 | 0.15191
| 0.25 |  |  | 0.53912 | 0.44165 | 0.34615 | 0.28883 | 0.13259
| 0.3 |  |  | 0.57032 | 0.43617 | 0.34766 | 0.28208 | 0.12955
| 0.35 |  |  | 0.59427 | 0.43262 | 0.34469 | 0.27113 | 0.13658
| 0.4 |  |  | 0.60914 | 0.42806 | 0.33782 | 0.25351 | 0.14906
| 0.45 |  |  | 0.61467 | 0.42148 | 0.32734 | 0.23019 | 0.16378
| 0.5 |  |  | 0.6114 | 0.41305 | 0.3134 | 0.20358 | 0.17861
| 0.55 |  |  | 0.60013 | 0.4035 | 0.29608 | 0.17611 | 0.19227
| 0.6 |  |  | 0.58145 | 0.39358 | 0.27545 | 0.14928 | 0.20408
| 0.65 |  |  | 0.55543 | 0.3838 | 0.25171 | 0.12338 | 0.21368
| 0.7 |  |  | 0.52142 | 0.37408 | 0.22526 | 0.097701 | 0.2208
| 0.75 |  |  | 0.47803 | 0.36375 | 0.19677 | 0.071247 | 0.22498
| 0.8 |  |  | 0.42318 | 0.35153 | 0.16731 | 0.044111 | 0.22533
| 0.85 |  |  | 0.35436 | 0.33573 | 0.13841 | 0.019326 | 0.22023
| 0.9 |  |  | 0.26896 | 0.31451 | 0.11218 | 0.0052885 | 0.20713
| 0.95 |  |  | 0.16474 | 0.28636 | 0.091377 | 0.01874 | 0.18227
| 1 |  |  | 0.0405 | 0.2506 | 0.0795 | 0.0883 | 0.1404
Column for x values
| Volume Flow p.u. |  | Hours Running | Damper(Back') | p.u. Watt-Hr
| 0.2 |  | 0 | 0.50488 | 0
| 0.25 |  | 0 | 0.53912 | 0
| 0.3 |  | 0 | 0.57032 | 0
| 0.35 |  | 0 | 0.59427 | 0
| 0.4 |  | 0 | 0.60914 | 0
| 0.45 |  | 0 | 0.61467 | 0
| 0.5 |  | 0 | 0.6114 | 0
| 0.55 |  | 0 | 0.60013 | 0
| 0.6 |  | 0 | 0.58145 | 0
| 0.65 |  | 0 | 0.55543 | 0
| 0.7 |  | 0 | 0.52142 | 0
| 0.75 |  | 0 | 0.47803 | 0
| 0.8 |  | 832 | 0.42318 | 352.085
| 0.85 |  | 0 | 0.35436 | 0
| 0.9 |  | 0 | 0.26896 | 0
| 0.95 |  | 0 | 0.16474 | 0
| 1 |  | 0 | 0.0405 | 0
[5 empty] | 352.085 | p.u. Watt-Hr
[5 empty] | 45894.2851 | kW-hr saved per year
Column for x values
| Volume Flow p.u. |  | Hours Running | Damper(Fwd) | p.u. Watt-Hr
| 0.2 |  | 0 | 0.45482 | 0
| 0.25 |  | 0 | 0.44165 | 0
| 0.3 |  | 0 | 0.43617 | 0
| 0.35 |  | 0 | 0.43262 | 0
| 0.4 |  | 0 | 0.42806 | 0
| 0.45 |  | 0 | 0.42148 | 0
| 0.5 |  | 0 | 0.41305 | 0
| 0.55 |  | 0 | 0.4035 | 0
| 0.6 |  | 0 | 0.39358 | 0
| 0.65 |  | 0 | 0.3838 | 0
| 0.7 |  | 0 | 0.37408 | 0
| 0.75 |  | 0 | 0.36375 | 0
| 0.8 |  | 832 | 0.35153 | 292.4725
| 0.85 |  | 0 | 0.33573 | 0
| 0.9 |  | 0 | 0.31451 | 0
| 0.95 |  | 0 | 0.28636 | 0
| 1 |  | 0 | 0.2506 | 0
[5 empty] | 292.4725 | p.u. Watt-Hr
[5 empty] | 38123.7896 | kW-hr saved per year
Column for x values
| Volume Flow p.u. |  | Hours Running | Inlet Guide Vane | p.u. Watt-Hr
| 0.2 |  | 0 | 0.33924 | 0
| 0.25 |  | 0 | 0.34615 | 0
| 0.3 |  | 0 | 0.34766 | 0
| 0.35 |  | 0 | 0.34469 | 0
| 0.4 |  | 0 | 0.33782 | 0
| 0.45 |  | 0 | 0.32734 | 0
| 0.5 |  | 0 | 0.3134 | 0
| 0.55 |  | 0 | 0.29608 | 0
| 0.6 |  | 0 | 0.27545 | 0
| 0.65 |  | 0 | 0.25171 | 0
| 0.7 |  | 0 | 0.22526 | 0
| 0.75 |  | 0 | 0.19677 | 0
| 0.8 |  | 832 | 0.16731 | 139.1992
| 0.85 |  | 0 | 0.13841 | 0
| 0.9 |  | 0 | 0.11218 | 0
| 0.95 |  | 0 | 0.091377 | 0
| 1 |  | 0 | 0.0795 | 0
[5 empty] | 139.1992 | p.u. Watt-Hr
18144.618
Column for x values
| Volume Flow p.u. |  | Hours Running | Disc throttle | p.u. Watt-Hr
| 0.2 |  | 0 | 0.29986 | 0
| 0.25 |  | 0 | 0.28883 | 0
| 0.3 |  | 0 | 0.28208 | 0
| 0.35 |  | 0 | 0.27113 | 0
| 0.4 |  | 0 | 0.25351 | 0
| 0.45 |  | 0 | 0.23019 | 0
| 0.5 |  | 0 | 0.20358 | 0
| 0.55 |  | 0 | 0.17611 | 0
| 0.6 |  | 0 | 0.14928 | 0
| 0.65 |  | 0 | 0.12338 | 0
| 0.7 |  | 0 | 0.097701 | 0
| 0.75 |  | 0 | 0.071247 | 0
| 0.8 |  | 832 | 0.044111 | 36.7007
| 0.85 |  | 0 | 0.019326 | 0
| 0.9 |  | 0 | 0.0052885 | 0
| 0.95 |  | 0 | 0.01874 | 0
| 1 |  | 0 | 0.0883 | 0
[5 empty] | 36.7007 | p.u. Watt-Hr
4783.9334
Column for x values
| Volume Flow p.u. |  | Hours Running | ECC | p.u. Watt-Hr
| 0.2 |  | 0 | 0.15191 | 0
| 0.25 |  | 0 | 0.13259 | 0
| 0.3 |  | 0 | 0.12955 | 0
| 0.35 |  | 0 | 0.13658 | 0
| 0.4 |  | 0 | 0.14906 | 0
| 0.45 |  | 0 | 0.16378 | 0
| 0.5 |  | 0 | 0.17861 | 0
| 0.55 |  | 0 | 0.19227 | 0
| 0.6 |  | 0 | 0.20408 | 0
| 0.65 |  | 0 | 0.21368 | 0
| 0.7 |  | 0 | 0.2208 | 0
| 0.75 |  | 0 | 0.22498 | 0
| 0.8 |  | 832 | 0.22533 | 187.471
| 0.85 |  | 0 | 0.22023 | 0
| 0.9 |  | 0 | 0.20713 | 0
| 0.95 |  | 0 | 0.18227 | 0
| 1 |  | 0 | 0.1404 | 0
[5 empty] | 187.471 | p.u. Watt-Hr
24436.8456
| Cost of Inverter (£) | 0 | 1950
| 0 | 0 | 0
| Cost of Installation (£) | 0 | 500
| Total cost |  | 2450
Column for x values
| Volume Flow p.u. |  | Hours Running | Pump C. Flow | p.u. Watt-Hr
| 0.2 |  | 0 | 0.92882 | 0
| 0.25 |  | 0 | 0.91623 | 0
| 0.3 |  | 0 | 0.90301 | 0
| 0.35 |  | 0 | 0.88687 | 0
| 0.4 |  | 0 | 0.86602 | 0
| 0.45 |  | 0 | 0.83908 | 0
| 0.5 |  | 0 | 0.80489 | 0
| 0.55 |  | 0 | 0.76245 | 0
| 0.6 |  | 0 | 0.71087 | 0
| 0.65 |  | 0 | 0.64934 | 0
| 0.7 |  | 0 | 0.57709 | 0
| 0.75 |  | 0 | 0.49349 | 0
| 0.8 |  | 832 | 0.39805 | 331.176
| 0.85 |  | 0 | 0.29055 | 0
| 0.9 |  | 0 | 0.17116 | 0
| 0.95 |  | 0 | 0.04057 | 0
| 1 |  | 0 | -0.0998 | 0
331.176
43168.7971
Note on B35: Flow Value for which power saving is to be calculated
Note on B57: Flow Value for which power saving is to be calculated
Note on B80: Flow Value for which power saving is to be calculated
Note on B103: Flow Value for which power saving is to be calculated
Note on B126: Flow Value for which power saving is to be calculated
Note on B149: Flow Value for which power saving is to be calculated